## DB-A
GROUND FLOOR DISTRIBUTION BOARD (DB-A)
Location: | KITCHEN | [12 empty] | Type: | 63A 8-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-A
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
AS3 - SOCKET POINTS | 3 x 2.5 | 5 | 250 | 1250 | 0.45 | 562.5 |  |  | 1 | 30 | 20 | 13 | 1200 |  |  | 0.4 | 3000 | 3000 | 1 | 3 x 6.0 | ACCU1
AL3 - LIGHTING POINTS | 2 x 1.5 | 9 | 100 | 900 | 0.45 |  | 405 |  | 2 | 10 | 10 | 14 |  | 495 |  | 0.45 | 1100 | 100 | 11 | 2 x 1.5 | AL4 - LIGHTING POINTS
AL5 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  |  | 450 | 3 | 10 | 10 | 15 |  |  | 450 | 0.45 | 1000 | 100 | 10 | 2 x 1.5 | AL6 - LIGHTING POINTS
AWH1 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 20 | 16 | 1360 |  |  | 0.8 | 1700 | 1700 | 1 | 3 x 4.0 | AAC2 - 20A SWITCH OUTLET
AS1 - SOCKET POINTS | 3 x 2.5 | 6 | 250 | 1500 | 0.45 |  | 675 |  | 5 | 30 | 20 | 17 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | AAC1 - 20A SWITCH OUTLET
AS2 - SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 6 | 30 | 20 | 18 |  |  | 680 | 0.8 | 850 | 850 | 1 | 3 x 4.0 | AAC3 - 20A SWITCH OUTLET
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 | 0 |  |  | 7 | 30 | 20 | 19 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | AAC4 - 20A SWITCH OUTLET
AS4 - SOCKET POINTS | 3 x 2.5 | 3 | 250 | 750 | 0.45 |  | 337.5 |  | 8 | 30 | 20 | 20 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | AAC5 - 20A SWITCH OUTLET
AL1 - LIGHTING POINTS | 2 x 1.5 | 15 | 100 | 1500 | 0.45 |  |  | 675 | 9 | 10 | 20 | 21 |  |  | 680 | 0.8 | 850 | 850 | 1 | 3 x 4.0 | AAC6 - 20A SWITCH OUTLET
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  | 10 | 30 | 30 | 22 | 0 |  |  | 0.4 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
AWH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 |  | 1200 |  | 11 | 20 | 30 | 23 |  | 450 |  | 0.45 | 1000 | 250 | 4 | 3 x 2.5 | AS5 - SOCKET POINTS
AWH3 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 |  |  | 1200 | 12 | 20 | 10 | 24 |  |  | 405 | 0.45 | 900 | 100 | 9 | 2 x 1.5 | AL2 - LIGHTING POINTS
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 2 x 1.5 | 0 | 100 | 0 | 0.45 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 12400 |  | 1762.5 | 2617.5 | 2775 |  |  |  |  | 3240 | 2305 | 2215 |  | 12950
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 10mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 5002.5 |  | 4922.5 | 4990 | [5 empty] | 1 x 10mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 15415 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 19268.75 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 26.9 |  | A

## DB-B
FIRST FLOOR DISTRIBUTION BOARD (DB-B)
Location: | KITCHEN | [12 empty] | Type: | 63A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-B
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
BL1 - LIGHTING POINTS | 2 x 1.5 | 15 | 100 | 1500 | 0.45 | 675 |  |  | 1 | 10 | 20 | 10 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | BAC4 - 20A SWITCH OUTLET
BWH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 |  | 1200 |  | 2 | 20 | 10 | 11 |  | 495 |  | 0.45 | 1100 | 100 | 11 | 2 x 1.5 | BL4 - LIGHTING POINTS
BL5 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  |  | 450 | 3 | 10 | 10 | 12 |  |  | 450 | 0.45 | 1000 | 100 | 10 | 2 x 1.5 | BL6 - LIGHTING POINTS
BWH1 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 10 | 13 | 360 |  |  | 0.45 | 800 | 100 | 8 | 2 x 1.5 | BL2 - LIGHTING POINTS
BAC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 5 | 20 | 20 | 14 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | BAC1 - 20A SWITCH OUTLET
BS2 - SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 6 | 30 | 30 | 15 |  |  | 337.5 | 0.45 | 750 | 250 | 3 | 3 x 2.5 | BS4 - SOCKET POINTS
BS1 - SOCKET POINTS | 3 x 2.5 | 6 | 250 | 1500 | 0.45 | 675 |  |  | 7 | 30 | 20 | 16 | 0 |  |  | 0.8 | 0 | 850 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 850 | 0 | 0.8 |  | 0 |  | 8 | 20 | 20 | 17 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | BAC5 - 20A SWITCH OUTLET
BS3 - SOCKET POINTS | 3 x 2.5 | 5 | 250 | 1250 | 0.45 |  |  | 562.5 | 9 | 30 | 20 | 18 |  |  | 1360 | 0.8 | 1700 | 1700 | 1 | 3 x 4.0 | BAC2 - 20A SWITCH OUTLET
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.4 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.8 | 0 | 850 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  |  | 0 |  | 20 | 10 |  |  |  | 0 | 0.45 | 0 | 100 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1700 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 10100 |  | 2550 | 1880 | 1462.5 |  |  |  |  | 1040 | 1855 | 2147.5 |  | 7900
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 10mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3590 |  | 3735 | 3610 | [5 empty] | 1 x 10mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11435 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14293.75 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 19.9 |  | A

## DB-C
FIRST FLOOR DISTRIBUTION BOARD (DB-C)
Location: | KITCHEN | [12 empty] | Type: | 63A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-C
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
CL1 - LIGHTING POINTS | 2 x 1.5 | 15 | 100 | 1500 | 0.45 | 675 |  |  | 1 | 10 | 20 | 10 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | CAC4 - 20A SWITCH OUTLET
CWH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 |  | 1200 |  | 2 | 20 | 10 | 11 |  | 495 |  | 0.45 | 1100 | 100 | 11 | 2 x 1.5 | CL4 - LIGHTING POINTS
CL5 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  |  | 450 | 3 | 10 | 10 | 12 |  |  | 450 | 0.45 | 1000 | 100 | 10 | 2 x 1.5 | CL6 - LIGHTING POINTS
CWH1 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 10 | 13 | 360 |  |  | 0.45 | 800 | 100 | 8 | 2 x 1.5 | CL2 - LIGHTING POINTS
CAC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 5 | 20 | 20 | 14 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | CAC1 - 20A SWITCH OUTLET
CS2- SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 6 | 30 | 30 | 15 |  |  | 337.5 | 0.45 | 750 | 250 | 3 | 3 x 2.5 | CS4 - SOCKET POINTS
CS1 - SOCKET POINTS | 3 x 2.5 | 6 | 250 | 1500 | 0.45 | 675 |  |  | 7 | 30 | 20 | 16 | 0 |  |  | 0.8 | 0 | 850 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 850 | 0 | 0.8 |  | 0 |  | 8 | 20 | 20 | 17 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | CAC5 - 20A SWITCH OUTLET
CS3 - SOCKET POINTS | 3 x 2.5 | 5 | 250 | 1250 | 0.45 |  |  | 562.5 | 9 | 30 | 20 | 18 |  |  | 1360 | 0.8 | 1700 | 1700 | 1 | 3 x 4.0 | CAC2 - 20A SWITCH OUTLET
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.4 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.8 | 0 | 850 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  |  | 0 |  | 20 | 10 |  |  |  | 0 | 0.45 | 0 | 100 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1700 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 10100 |  | 2550 | 1880 | 1462.5 |  |  |  |  | 1040 | 1855 | 2147.5 |  | 7900
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 10mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3590 |  | 3735 | 3610 | [5 empty] | 1 x 10mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11435 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14293.75 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 19.9 |  | A

## DB-D
SECOND FLOOR DISTRIBUTION BOARD (DB-D)
Location: | KITCHEN | [12 empty] | Type: | 63A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-D
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
DL1 - LIGHTING POINTS | 2 x 1.5 | 15 | 100 | 1500 | 0.45 | 675 |  |  | 1 | 10 | 20 | 10 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | DAC4 - 20A SWITCH OUTLET
DWH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 |  | 1200 |  | 2 | 20 | 10 | 11 |  | 495 |  | 0.45 | 1100 | 100 | 11 | 2 x 1.5 | DL4 - LIGHTING POINTS
DL5 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  |  | 450 | 3 | 10 | 10 | 12 |  |  | 450 | 0.45 | 1000 | 100 | 10 | 2 x 1.5 | DL6 - LIGHTING POINTS
DWH1 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 10 | 13 | 360 |  |  | 0.45 | 800 | 100 | 8 | 2 x 1.5 | DL2 - LIGHTING POINTS
DAC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 5 | 20 | 20 | 14 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | DAC1 - 20A SWITCH OUTLET
DS2- SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 6 | 30 | 30 | 15 |  |  | 337.5 | 0.45 | 750 | 250 | 3 | 3 x 2.5 | DS4 - SOCKET POINTS
DS1 - SOCKET POINTS | 3 x 2.5 | 6 | 250 | 1500 | 0.45 | 675 |  |  | 7 | 30 | 20 | 16 | 0 |  |  | 0.8 | 0 | 850 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 850 | 0 | 0.8 |  | 0 |  | 8 | 20 | 20 | 17 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | DAC5 - 20A SWITCH OUTLET
DS3 - SOCKET POINTS | 3 x 2.5 | 5 | 250 | 1250 | 0.45 |  |  | 562.5 | 9 | 30 | 20 | 18 |  |  | 1360 | 0.8 | 1700 | 1700 | 1 | 3 x 4.0 | DAC2 - 20A SWITCH OUTLET
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.4 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.8 | 0 | 850 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  |  | 0 |  | 20 | 10 |  |  |  | 0 | 0.45 | 0 | 100 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1700 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 10100 |  | 2550 | 1880 | 1462.5 |  |  |  |  | 1040 | 1855 | 2147.5 |  | 7900
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 10mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3590 |  | 3735 | 3610 | [5 empty] | 1 x 10mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11435 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14293.75 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 19.9 |  | A

## DB-E
SECOND FLOOR DISTRIBUTION BOARD (DB-E)
Location: | KITCHEN | [12 empty] | Type: | 63A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-E
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
EL1 - LIGHTING POINTS | 2 x 1.5 | 15 | 100 | 1500 | 0.45 | 675 |  |  | 1 | 10 | 20 | 10 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | EAC4 - 20A SWITCH OUTLET
EWH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 |  | 1200 |  | 2 | 20 | 10 | 11 |  | 495 |  | 0.45 | 1100 | 100 | 11 | 2 x 1.5 | EL4 - LIGHTING POINTS
EL5 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  |  | 450 | 3 | 10 | 10 | 12 |  |  | 450 | 0.45 | 1000 | 100 | 10 | 2 x 1.5 | EL6 - LIGHTING POINTS
EWH1 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 10 | 13 | 360 |  |  | 0.45 | 800 | 100 | 8 | 2 x 1.5 | EL2 - LIGHTING POINTS
EAC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 5 | 20 | 20 | 14 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | EAC1 - 20A SWITCH OUTLET
ES2- SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 6 | 30 | 30 | 15 |  |  | 337.5 | 0.45 | 750 | 250 | 3 | 3 x 2.5 | ES4 - SOCKET POINTS
ES1 - SOCKET POINTS | 3 x 2.5 | 6 | 250 | 1500 | 0.45 | 675 |  |  | 7 | 30 | 20 | 16 | 0 |  |  | 0.8 | 0 | 850 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 850 | 0 | 0.8 |  | 0 |  | 8 | 20 | 20 | 17 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | EAC5 - 20A SWITCH OUTLET
ES3 - SOCKET POINTS | 3 x 2.5 | 5 | 250 | 1250 | 0.45 |  |  | 562.5 | 9 | 30 | 20 | 18 |  |  | 1360 | 0.8 | 1700 | 1700 | 1 | 3 x 4.0 | EAC2 - 20A SWITCH OUTLET
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.4 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.8 | 0 | 850 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  |  | 0 |  | 20 | 10 |  |  |  | 0 | 0.45 | 0 | 100 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.45 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1700 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 10100 |  | 2550 | 1880 | 1462.5 |  |  |  |  | 1040 | 1855 | 2147.5 |  | 7900
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 10mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3590 |  | 3735 | 3610 | [5 empty] | 1 x 10mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11435 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14293.75 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 19.9 |  | A