## DB-A
GROUND FLOOR DISTRIBUTION BOARD (DB-A)
Location: | STORE | [12 empty] | Type: | 63A 8-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-A
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
SPARE | 2 x 1.5 | 0 | 100 | 0 | 0.45 | 0 |  |  | 1 | 10 | 15 | 13 | 810 |  |  | 0.45 | 1800 | 100 | 18 | 2 x 2.5 | AL2 - LIGHTING
AL3 - LIGHTING | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  | 450 |  | 2 | 10 | 10 | 14 |  | 450 |  | 0.45 | 1000 | 1000 | 1 | 2 x 1.5 | AL4 - LIGHTING
AL5 - LIGHTING | 2 x 2.5 | 12 | 100 | 1200 | 0.45 |  |  | 540 | 3 | 15 | 15 | 15 |  |  | 585 | 0.45 | 1300 | 100 | 13 | 2 x 2.5 | AL6 - LIGHTING
AL7 - LIGHTING | 2 x 2.5 | 17 | 100 | 1700 | 0.45 | 765 |  |  | 4 | 15 | 15 | 16 | 585 |  |  | 0.45 | 1300 | 100 | 13 | 2 x 2.5 | AL8 - LIGHTING
AL9 - LIGHTING | 2 x 2.5 | 9 | 100 | 900 | 0.45 |  | 405 |  | 5 | 15 | 15 | 17 |  | 990 |  | 0.45 | 2200 | 100 | 22 | 2 x 2.5 | AL10 - LIGHTING
AL11 - LIGHTING | 2 x 2.5 | 23 | 100 | 2300 | 0.45 |  |  | 1035 | 6 | 15 | 15 | 18 |  |  | 855 | 0.45 | 1900 | 100 | 19 | 2 x 2.5 | AL12 - LIGHTING
AL13 - LIGHTING | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 | 450 |  |  | 7 | 10 | 15 | 19 | 630 |  |  | 0.45 | 1400 | 100 | 14 | 2 x 2.5 | AL14 - LIGHTING
AL15 - LIGHTING | 2 x 2.5 | 20 | 100 | 2000 | 0.45 |  | 900 |  | 8 | 15 | 15 | 20 |  | 1125 |  | 0.45 | 2500 | 100 | 25 | 2 x 2.5 | AL16 - LIGHTING
AL17 - LIGHTING | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  |  | 450 | 9 | 10 | 10 | 21 |  |  | 450 | 0.45 | 1000 | 1000 | 1 | 2 x 1.5 | AL18 - LIGHTING
AL19 - LIGHTING | 2 x 2.5 | 19 | 100 | 1900 | 0.45 | 855 |  |  | 10 | 15 | 15 | 22 | 675 |  |  | 0.45 | 1500 | 100 | 15 | 2 x 2.5 | AL20 - LIGHTING
SPARE | 2 x 1.5 | 0 | 100 | 0 | 0.45 |  | 0 |  | 11 | 10 | 30 | 23 |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 4.0 | SPARE
AL1 - LIGHTING | 2 x 2.5 | 20 | 100 | 2000 | 0.45 |  |  | 900 | 12 | 15 | 10 | 24 |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 15000 |  | 2070 | 1755 | 2925 |  |  |  |  | 2700 | 2565 | 1890 |  | 15900
* RING MAIN FINAL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 4770 |  | 4320 | 4815 | [5 empty] | 1 x 4mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 14405 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 18006.25 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 25.1 |  | A

## DB-B
GROUND FLOOR DISTRIBUTION BOARD (DB-B)
Location: | STORE | [12 empty] | Type: | 63A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-B
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
BS1 - 13A SOCKET OUTLET | 3 x 2.5 | 8 | 250 | 2000 | 0.5 | 1000 |  |  | 1 | 30 | 30 | 10 | 875 |  |  | 0.5 | 1750 | 250 | 7 | 3 x 2.5 | BS6 - 13A SOCKET OUTLET
BS3 - 13A SOCKET OUTLET | 3 x 2.5 | 8 | 250 | 2000 | 0.5 |  | 1000 |  | 2 | 30 | 30 | 11 |  | 1250 |  | 0.5 | 2500 | 250 | 10 | 3 x 2.5 | BS4 - 13A SOCKET OUTLET
BS5 - 13A SOCKET OUTLET | 3 x 2.5 | 7 | 250 | 1750 | 0.5 |  |  | 875 | 3 | 30 | 30 | 12 |  |  | 625 | 0.5 | 1250 | 250 | 5 | 3 x 2.5 | BS2 - 13A SOCKET OUTLET
BS7 - 13A SOCKET OUTLET | 3 x 2.5 | 7 | 250 | 1750 | 0.5 | 875 |  |  | 4 | 30 | 30 | 13 | 625 |  |  | 0.5 | 1250 | 250 | 5 | 3 x 2.5 | BS8 - 13A SOCKET OUTLET
BS9 - 13A SOCKET OUTLET | 3 x 2.5 | 9 | 250 | 2250 | 0.5 |  | 1125 |  | 5 | 30 | 30 | 14 |  | 625 |  | 0.5 | 1250 | 250 | 5 | 3 x 2.5 | BS10 - 13A SOCKET OUTLET
BS11 - 13A SOCKET OUTLET | 3 x 2.5 | 12 | 250 | 3000 | 0.5 |  |  | 1500 | 6 | 30 | 30 | 15 |  |  | 1000 | 0.5 | 2000 | 250 | 8 | 3 x 2.5 | BS12 - 13A SOCKET OUTLET
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  | 7 | 30 | 30 | 16 | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 |  | 0 |  | 8 | 30 | 30 | 17 |  | 0 |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 |  |  | 0 | 9 | 30 | 30 | 18 |  |  | 0 | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 100 | 0 | 0.45 |  | 0 |  |  | 10 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 4.0 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 12750 |  | 1875 | 2125 | 2375 |  |  |  |  | 1500 | 1875 | 1625 |  | 10000
* RING MAIN FINAL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3375 |  | 4000 | 4000 | [5 empty] | 1 x 4mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11875 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14843.75 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 20.7 |  | A

## DB-C
GROUND FLOOR DISTRIBUTION BOARD (DB-C)
Location: | STORE | [12 empty] | Type: | 63A 8-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-C
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
CAC1 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 65 | 65 | 0.8 | 52 |  |  | 1 | 15 | 15 | 13 | 448 |  |  | 0.8 | 560 | 560 | 1 | 3 x 2.5 | CAC2 - 20A SWITCH OUTLET
CAC3 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 560 | 560 | 0.8 |  | 448 |  | 2 | 15 | 15 | 14 |  | 448 |  | 0.8 | 560 | 560 | 1 | 3 x 2.5 | CAC4 - 20A SWITCH OUTLET
CAC5 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 490 | 490 | 0.8 |  |  | 392 | 3 | 15 | 15 | 15 |  |  | 448 | 0.8 | 560 | 560 | 1 | 3 x 2.5 | CAC6 - 20A SWITCH OUTLET
CAC12 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 560 | 560 | 0.8 | 448 |  |  | 4 | 15 | 15 | 16 | 52 |  |  | 0.8 | 65 | 65 | 1 | 3 x 2.5 | CAC8 - 20A SWITCH OUTLET
CAC9 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 |  | 92.8 |  | 5 | 15 | 15 | 17 |  | 92.8 |  | 0.8 | 116 | 116 | 1 | 3 x 2.5 | CAC10 - 20A SWITCH OUTLET
CP1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  |  | 800 | 6 | 15 | 15 | 18 |  |  | 92.8 | 0.8 | 116 | 116 | 1 | 3 x 2.5 | CAC7 - 20A SWITCH OUTLET
CAC13 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 560 | 560 | 0.8 | 448 |  |  | 7 | 15 | 15 | 19 | 320 |  |  | 0.8 | 400 | 400 | 1 | 3 x 2.5 | C-ERV1 - ENERGY RECOVERY UNIT
CAC11 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 560 | 560 | 0.8 |  | 448 |  | 8 | 15 | 30 | 20 |  | 800 |  | 0.4 | 2000 | 2000 | 1 | 3 x 6.0 | C-CCU1 - COOKER UNIT
CP2 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  |  | 800 | 9 | 15 | 15 | 21 |  |  | 320 | 0.8 | 400 | 400 | 1 | 3 x 4.0 | C-ERV2 - ENERGY RECOVERY UNIT
CP3 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 | 800 |  |  | 10 | 15 | 20 | 22 | 0 |  |  | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 6.0 | 0 | 3000 | 0 | 0.4 |  | 0 |  | 11 | 30 | 15 | 23 |  | 0 |  | 0.8 | 0 | 400 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 400 | 0 | 0.8 |  |  | 0 | 12 | 15 | 15 | 24 |  |  | 0 | 0.8 | 0 | 116 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 8911 |  | 1748 | 988.8 | 1992 |  |  |  |  | 820 | 1340.8 | 860.8 |  | 4777
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 10mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 2568 |  | 2329.6 | 2852.8 | [5 empty] | 1 x 10mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 8250.4 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 10313 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 14.4 |  | A

## DB-D
FIRST FLOOR DISTRIBUTION BOARD (DB-D)
Location: | PANEL ROOM | [12 empty] | Type: | 63A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-D
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
DL1 - LIGHTING | 2 x 2.5 | 20 | 100 | 2000 | 0.45 | 900 |  |  | 1 | 15 | 15 | 10 | 900 |  |  | 0.45 | 2000 | 100 | 20 | 2 x 2.5 | DL2 - LIGHTING
DL3 - LIGHTING | 2 x 2.5 | 20 | 100 | 2000 | 0.45 |  | 900 |  | 2 | 15 | 15 | 11 |  | 1125 |  | 0.45 | 2500 | 100 | 25 | 2 x 2.5 | DL4 - LIGHTING
DL5 - LIGHTING | 2 x 2.5 | 15 | 100 | 1500 | 0.45 |  |  | 675 | 3 | 15 | 15 | 12 |  |  | 720 | 0.45 | 1600 | 100 | 16 | 2 x 2.5 | DL6 - LIGHTING
DL10 - LIGHTING | 2 x 2.5 | 6 | 100 | 600 | 0.45 | 270 |  |  | 4 | 15 | 10 | 13 | 450 |  |  | 0.45 | 1000 | 1000 | 1 | 2 x 2.5 | DL8 - LIGHTING
DL9 - LIGHTING | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  | 450 |  | 5 | 10 | 15 | 14 |  | 0 |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
DL11 - LIGHTING | 2 x 2.5 | 22 | 100 | 2200 | 0.45 |  |  | 990 | 6 | 15 | 15 | 15 |  |  | 1035 | 0.45 | 2300 | 100 | 23 | 2 x 2.5 | DL12 - LIGHTING
DL13 - LIGHTING | 2 x 2.5 | 17 | 100 | 1700 | 0.45 | 765 |  |  | 7 | 15 | 10 | 16 | 450 |  |  | 0.45 | 1000 | 1000 | 1 | 2 x 2.5 | DL14 - LIGHTING
DL7 - LIGHTING | 2 x 2.5 | 27 | 100 | 2700 | 0.45 |  | 1215 |  | 8 | 15 | 15 | 17 |  | 0 |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 | 9 | 15 | 15 | 18 |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 | 0 |  |  |  | 15 | 15 |  | 0 |  |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 |  | 0 |  |  | 10 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 |  |  | 0 |  | 15 | 10 |  |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 2.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 13700 |  | 1935 | 2565 | 1665 |  |  |  |  | 1800 | 1125 | 1755 |  | 10400
* RING MAIN FINAL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3735 |  | 3690 | 3420 | [5 empty] | 1 x 4mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11345 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14181.25 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 19.8 |  | A

## DB-E
FIRST FLOOR DISTRIBUTION BOARD (DB-E)
Location: | PANEL ROOM | [12 empty] | Type: | 63A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-E
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
ES1 - 13A SOCKET OUTLET | 3 x 2.5 | 7 | 250 | 1750 | 0.5 | 875 |  |  | 1 | 30 | 30 | 10 | 1125 |  |  | 0.5 | 2250 | 250 | 9 | 3 x 2.5 | ES2 - 13A SOCKET OUTLET
ES3 - 13A SOCKET OUTLET | 3 x 2.5 | 8 | 250 | 2000 | 0.5 |  | 1000 |  | 2 | 30 | 30 | 11 |  | 1375 |  | 0.5 | 2750 | 250 | 11 | 3 x 2.5 | ES4 - 13A SOCKET OUTLET
ES5 - 13A SOCKET OUTLET | 3 x 2.5 | 8 | 250 | 2000 | 0.5 |  |  | 1000 | 3 | 30 | 30 | 12 |  |  | 375 | 0.5 | 750 | 250 | 3 | 3 x 2.5 | ES6 - 13A SOCKET OUTLET
ES7 - 13A SOCKET OUTLET | 3 x 2.5 | 8 | 250 | 2000 | 0.5 | 1000 |  |  | 4 | 30 | 30 | 13 | 750 |  |  | 0.5 | 1500 | 250 | 6 | 3 x 2.5 | ES8 - 13A SOCKET OUTLET
ES9 - 13A SOCKET OUTLET | 3 x 2.5 | 4 | 250 | 1000 | 0.5 |  | 500 |  | 5 | 30 | 30 | 14 |  | 1000 |  | 0.5 | 2000 | 250 | 8 | 3 x 2.5 | ES10 - 13A SOCKET OUTLET
ES11 - 13A SOCKET OUTLET | 3 x 2.5 | 13 | 250 | 3250 | 0.5 |  |  | 1625 | 6 | 30 | 30 | 15 |  |  | 625 | 0.5 | 1250 | 250 | 5 | 3 x 2.5 | ES12 - 13A SOCKET OUTLET
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  | 7 | 30 | 30 | 16 | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 |  | 0 |  | 8 | 30 | 30 | 17 |  | 0 |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 |  |  | 0 | 9 | 30 | 30 | 18 |  |  | 0 | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 100 | 0 | 0.45 |  | 0 |  |  | 10 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 4.0 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 12000 |  | 1875 | 1500 | 2625 |  |  |  |  | 1875 | 2375 | 1000 |  | 10500
* RING MAIN FINAL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3750 |  | 3875 | 3625 | [5 empty] | 1 x 4mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11750 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14687.5 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 20.5 |  | A

## DB-G
FIRST FLOOR DISTRIBUTION BOARD (DB-G)
Location: | PANEL ROOM | [12 empty] | Type: | 63A 8-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-G
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
GAC1 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 560 | 560 | 0.8 | 448 |  |  | 1 | 15 | 15 | 13 | 448 |  |  | 0.8 | 560 | 560 | 1 | 3 x 2.5 | GAC2 - 20A SWITCH OUTLET
GAC3 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 |  | 92.8 |  | 2 | 15 | 15 | 14 |  | 92.8 |  | 0.8 | 116 | 116 | 1 | 3 x 2.5 | GAC6 - 20A SWITCH OUTLET
GAC5 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 |  |  | 92.8 | 3 | 15 | 15 | 15 |  |  | 44.8 | 0.8 | 56 | 56 | 1 | 3 x 2.5 | GAC4 - 20A SWITCH OUTLET
GAC7 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 56 | 56 | 0.8 | 44.8 |  |  | 4 | 15 | 15 | 16 | 448 |  |  | 0.8 | 560 | 560 | 1 | 3 x 2.5 | GAC8 - 20A SWITCH OUTLET
GAC11 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 560 | 560 | 0.8 |  | 448 |  | 5 | 15 | 15 | 17 |  | 448 |  | 0.8 | 560 | 560 | 1 | 3 x 2.5 | GAC10 - 20A SWITCH OUTLET
GAC9 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 |  |  | 92.8 | 6 | 15 | 15 | 18 |  |  | 448 | 0.8 | 560 | 560 | 1 | 3 x 2.5 | GAC12 - 20A SWITCH OUTLET
GAC13 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 | 92.8 |  |  | 7 | 15 | 15 | 19 | 44.8 |  |  | 0.8 | 56 | 56 | 1 | 3 x 2.5 | GAC14 - 20A SWITCH OUTLET
GAC15 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 |  | 92.8 |  | 8 | 15 | 15 | 20 |  | 92.8 |  | 0.8 | 116 | 116 | 1 | 3 x 2.5 | GAC16 - 20A SWITCH OUTLET
GAC17 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 56 | 56 | 0.8 |  |  | 44.8 | 9 | 15 | 20 | 21 |  |  | 1080 | 0.8 | 1350 | 1350 | 1 | 3 x 4.0 | GAC18 - 20A SWITCH OUTLET
G-ERV1 - ENERGY RECOVERY UNIT | 3 x 2.5 | 1 | 400 | 400 | 0.8 | 320 |  |  | 10 | 15 | 20 | 22 | 0 |  |  | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
G-ERV2 - ENERGY RECOVERY UNIT | 3 x 2.5 | 1 | 400 | 400 | 0.8 |  | 320 |  | 11 | 15 | 20 | 23 |  | 0 |  | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 116 | 0 | 0.8 |  |  | 0 | 12 | 15 | 20 | 24 |  |  | 0 | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 2612 |  | 905.6 | 953.6 | 230.4 |  |  |  |  | 940.8 | 633.6 | 1572.8 |  | 3934
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 1846.4 |  | 1587.2 | 1803.2 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 5736.8 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 7171 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 10 |  | A

## DB-H
SECOND FLOOR DISTRIBUTION BOARD (DB-H)
Location: | PANEL ROOM | [12 empty] | Type: | 63A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-H
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
HL1 - LIGHTING | 2 x 2.5 | 16 | 100 | 1600 | 0.45 | 720 |  |  | 1 | 15 | 15 | 10 | 720 |  |  | 0.45 | 1600 | 100 | 16 | 2 x 2.5 | HL2 - LIGHTING
HL3 - LIGHTING | 2 x 2.5 | 31 | 100 | 3100 | 0.45 |  | 1395 |  | 2 | 15 | 15 | 11 |  | 945 |  | 0.45 | 2100 | 100 | 21 | 2 x 2.5 | HL4 - LIGHTING
HL5 - LIGHTING | 2 x 2.5 | 15 | 100 | 1500 | 0.45 |  |  | 675 | 3 | 15 | 10 | 12 |  |  | 450 | 0.45 | 1000 | 100 | 1 | 2 x 1.5 | HL6 - LIGHTING
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 | 0 |  |  | 4 | 15 | 15 | 13 | 945 |  |  | 0.45 | 2100 | 100 | 21 | 2 x 2.5 | HL8 - LIGHTING
HL9 - LIGHTING | 2 x 2.5 | 17 | 100 | 1700 | 0.45 |  | 765 |  | 5 | 15 | 15 | 14 |  | 0 |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
HL11 - LIGHTING | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  |  | 450 | 6 | 10 | 10 | 15 |  |  | 450 | 0.45 | 1000 | 100 | 1 | 2 x 1.5 | HL12 - LIGHTING
HL13 - LIGHTING | 2 x 2.5 | 16 | 100 | 1600 | 0.45 | 720 |  |  | 7 | 15 | 15 | 16 | 0 |  |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 |  | 0 |  | 8 | 15 | 15 | 17 |  | 0 |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
HL7 - LIGHTING | 2 x 2.5 | 12 | 100 | 1200 | 0.45 |  |  | 540 | 9 | 15 | 15 | 18 |  |  | 585 | 0.45 | 1300 | 100 | 13 | 2 x 2.5 | HL10 - LIGHTING
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 | 0 |  |  |  | 15 | 15 |  | 0 |  |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 |  | 0 |  |  | 10 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 |  |  | 0 |  | 15 | 10 |  |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 2.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 11700 |  | 1440 | 2160 | 1665 |  |  |  |  | 1665 | 945 | 1485 |  | 9100
* RING MAIN FINAL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3105 |  | 3105 | 3150 | [5 empty] | 1 x 4mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 9860 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 12325 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 17.2 |  | A

## DB-J
SECOND FLOOR DISTRIBUTION BOARD (DB-J)
Location: | PANEL ROOM | [12 empty] | Type: | 63A 4-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-J
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  | 1 | 30 | 30 | 7 | 1000 |  |  | 0.5 | 2000 | 250 | 8 | 3 x 2.5 | JS2 - 13A SOCKET OUTLET
JS3 - 13A SOCKET OUTLET | 3 x 2.5 | 11 | 250 | 2750 | 0.5 |  | 1375 |  | 2 | 30 | 30 | 8 |  | 1250 |  | 0.5 | 2500 | 250 | 10 | 3 x 2.5 | JS4 - 13A SOCKET OUTLET
JS9 - 13A SOCKET OUTLET | 3 x 2.5 | 4 | 250 | 1000 | 0.5 |  |  | 500 | 3 | 30 | 30 | 9 |  |  | 1000 | 0.5 | 2000 | 250 | 8 | 3 x 2.5 | JS6 - 13A SOCKET OUTLET
JS7 - 13A SOCKET OUTLET | 3 x 2.5 | 9 | 250 | 2250 | 0.5 | 1125 |  |  | 4 | 30 | 30 | 10 | 500 |  |  | 0.5 | 1000 | 250 | 4 | 3 x 2.5 | JS8 - 13A SOCKET OUTLET
JS5 - 13A SOCKET OUTLET | 3 x 2.5 | 3 | 250 | 750 | 0.5 |  | 375 |  | 5 | 30 | 30 | 11 |  | 0 |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
JS1 - 13A SOCKET OUTLET | 3 x 2.5 | 11 | 250 | 2750 | 0.5 |  |  | 1375 | 6 | 30 | 30 | 12 |  |  | 0 | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 |  | 0 |  |  | 30 | 30 |  |  | 0 |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 |  |  | 0 |  | 30 | 30 |  |  |  | 0 | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.45 | 0 | 100 | 0 | 2 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 100 | 0 | 0.45 |  | 0 |  |  | 10 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 4.0 | SPARE
SPARE | 2 x 2.5 | 0 | 100 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 9500 |  | 1125 | 1750 | 1875 |  |  |  |  | 1500 | 1250 | 1000 |  | 7500
* RING MAIN FINAL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 2625 |  | 3000 | 2875 | [5 empty] | 1 x 4mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 9000 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 11250 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 15.7 |  | A

## DB-K
SECOND FLOOR DISTRIBUTION BOARD (DB-K)
Location: | PANEL ROOM | [12 empty] | Type: | 63A 8-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-K
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CP1
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
KAC1 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 56 | 56 | 0.8 | 44.8 |  |  | 1 | 15 | 15 | 13 | 0 |  |  | 0.8 | 0 | 116 | 0 | 3 x 2.5 | SPARE
KAC3 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 |  | 92.8 |  | 2 | 15 | 15 | 14 |  | 92.8 |  | 0.8 | 116 | 116 | 1 | 3 x 2.5 | KAC4 - 20A SWITCH OUTLET
SPARE | 3 x 2.5 | 0 | 116 | 0 | 0.8 |  |  | 0 | 3 | 15 | 15 | 15 |  |  | 92.8 | 0.8 | 116 | 116 | 1 | 3 x 2.5 | KAC2 - 20A SWITCH OUTLET
| 3 x 2.5 | 0 | 560 | 0 | 0.8 | 0 |  |  | 4 | 15 | 15 | 16 | 0 |  |  | 0.8 | 0 | 116 | 0 | 3 x 2.5 | SPARE
KAC9 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 |  | 92.8 |  | 5 | 15 | 15 | 17 |  | 92.8 |  | 0.8 | 116 | 116 | 1 | 3 x 2.5 | KAC10 - 20A SWITCH OUTLET
KAC11 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 560 | 560 | 0.8 |  |  | 448 | 6 | 15 | 15 | 18 |  |  | 92.8 | 0.8 | 116 | 116 | 1 | 3 x 2.5 | KAC8 - 20A SWITCH OUTLET
KAC15 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 | 92.8 |  |  | 7 | 15 | 15 | 19 | 0 |  |  | 0.8 | 0 | 116 | 0 | 3 x 2.5 | SPARE
KAC7 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 560 | 560 | 0.8 |  | 448 |  | 8 | 15 | 15 | 20 |  | 92.8 |  | 0.8 | 116 | 116 | 1 | 3 x 4.0 | KAC13 - 20A SWITCH OUTLET
K-ERV1 - ENERGY RECOVERY UNIT | 3 x 2.5 | 1 | 400 | 400 | 0.8 |  |  | 320 | 9 | 15 | 15 | 21 |  |  | 92.8 | 0.8 | 116 | 116 | 1 | 3 x 4.0 | KAC14 - 20A SWITCH OUTLET
K-ERV2 - ENERGY RECOVERY UNIT | 3 x 2.5 | 1 | 400 | 400 | 0.8 | 320 |  |  | 10 | 15 | 20 | 22 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | KAC12 - 20A SWITCH OUTLET
KAC5 - 20A SWITCH OUTLET | 3 x 2.5 | 1 | 116 | 116 | 0.8 |  | 92.8 |  | 11 | 15 | 15 | 23 |  | 92.8 |  | 0.8 | 116 | 116 | 1 | 3 x 2.5 | KAC6 - 20A SWITCH OUTLET
SPARE | 3 x 4.0 | 0 | 116 | 0 | 0.8 |  |  | 0 | 12 | 20 | 20 | 24 |  |  | 0 | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 2440 |  | 457.6 | 726.4 | 768 |  |  |  |  | 680 | 371.2 | 278.4 |  | 1662
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 63A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 1137.6 |  | 1097.6 | 1046.4 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 3781.6 |  | W
63A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 4727 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 6.6 |  | A