## DB-A
GROUND FLOOR DISTRIBUTION BOARD (DB-A)
Location: | POWER HOUSE | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-A
Cable Length(m) to ControlPanel | [13 empty] | Fed from | MDP
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
AL5 - LIGHTING | 2 x 1.5 | 8 | 100 | 800 | 0.45 | 360 |  |  | 1 | 10 | 10 | 10 | 450 |  |  | 0.45 | 1000 | 100 | 10 | 2 x 1.5 | AL2 - LIGHTING
AL3 - LIGHTING | 2 x 1.5 | 7 | 100 | 700 | 0.45 |  | 315 |  | 2 | 10 | 10 | 11 |  | 360 |  | 0.45 | 800 | 100 | 8 | 2 x 1.5 | AL6 - LIGHTING
AL1 - LIGHTING | 2 x 1.5 | 10 | 100 | 1000 | 0.45 |  |  | 450 | 3 | 10 | 10 | 12 |  |  | 765 | 0.45 | 1700 | 100 | 17 | 2 x 1.5 | AL4 - LIGHTING
AS1 - 13A SOCKET OUTLET | 3 x 2.5 | 6 | 250 | 1500 | 0.5 | 750 |  |  | 4 | 30 | 30 | 13 | 500 |  |  | 0.5 | 1000 | 250 | 4 | 3 x 2.5 | AS2 - 13A SOCKET OUTLET
AS3 - 13A SOCKET OUTLET | 3 x 2.5 | 7 | 250 | 1750 | 0.5 |  | 875 |  | 5 | 30 | 30 | 14 |  | 500 |  | 0.5 | 1000 | 250 | 4 | 3 x 2.5 | AS4 - 13A SOCKET OUTLET
AS5 - 13A SOCKET OUTLET | 3 x 2.5 | 4 | 250 | 1000 | 0.5 |  |  | 500 | 6 | 30 | 30 | 15 |  |  | 375 | 0.5 | 750 | 250 | 3 | 3 x 2.5 | AS6 - 13A SOCKET OUTLET
SPARE | 2 x 1.5 | 0 | 100 | 0 | 0.45 | 0 |  |  | 7 | 30 | 30 | 16 | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  | 8 | 30 | 10 | 17 |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 |  |  | 0 | 9 | 30 | 30 | 18 |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 2 x 1.5 | 0 | 100 | 0 | 0.45 | 0 |  |  |  | 10 | 30 |  | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 4.0 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 6750 |  | 1110 | 1190 | 950 |  |  |  |  | 950 | 860 | 1140 |  | 6250
* RING MAIN FINAL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 4mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 2060 |  | 2050 | 2090 | [5 empty] | 1 x 4mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 6700 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 8375 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 11.7 |  | A

## DB-B
GROUND FLOOR DISTRIBUTION BOARD (DB-B)
Location: | POWER HOUSE | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB-B
Cable Length(m) to ControlPanel | [13 empty] | Fed from | MDP
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
BAC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 1700 | 1700 | 0.8 | 1360 |  |  | 1 | 20 | 30 | 10 | 1200 |  |  | 0.4 | 3000 | 3000 | 1 | 3 x 6.0 | B-CCU2 - COOKER UNIT
BAC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 1700 | 1700 | 0.8 |  | 1360 |  | 2 | 20 | 20 | 11 |  | 1360 |  | 0.8 | 1700 | 1700 | 1 | 3 x 4.0 | BAC4 - 20A SWITCH OUTLET
BAC5 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 1700 | 1700 | 0.8 |  |  | 1360 | 3 | 20 | 20 | 12 |  |  | 680 | 0.8 | 850 | 850 | 1 | 3 x 4.0 | BAC6 - 20A SWITCH OUTLET
BP1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 | 800 |  |  | 4 | 15 | 15 | 13 | 800 |  |  | 0.4 | 2000 | 2000 | 1 | 3 x 4.0 | BP2 - 15A POWER SOCKET
BP3 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 15 | 14 |  | 800 |  | 0.4 | 2000 | 2000 | 1 | 3 x 4.0 | BP4 - 15A POWER SOCKET
B-CCU1 - COOKER UNIT | 3 x 6.0 | 1 | 3000 | 3000 | 0.4 |  |  | 1200 | 6 | 30 | 20 | 15 |  |  | 904 | 0.8 | 1130 | 1130 | 1 | 3 x 4.0 | BAC2 - 20A SWITCH OUTLET
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.4 | 0 |  |  | 7 | 20 | 20 | 16 | 0 |  |  | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  | 8 | 20 | 30 | 17 |  | 0 |  | 0.4 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 15 | 18 |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 12100 |  | 2160 | 2160 | 2560 |  |  |  |  | 2000 | 2160 | 1584 |  | 10680
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 4160 |  | 4320 | 4144 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 13124 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 16405 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 22.9 |  | A