## DB 1-A
GROUND FLOOR DISTRIBUTION BOARD (DB 1-A)
Location: | PANTRY | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB 1-A
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
1A-AC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 1700 | 1700 | 0.8 | 1360 |  |  | 1 | 20 | 20 | 10 | 1200 |  |  | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 1A-WH1
1A-AC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 2 | 20 | 20 | 11 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | 1A-AC2 - 20A SWITCH OUTLET
1A-P2 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  |  | 800 | 3 | 15 | 30 | 12 |  |  | 1200 | 0.4 | 3000 | 3000 | 1 | 3 x 6.0 | 1A-CCU1
1-AL1 - LIGHTING POINTS | 2 x 1.5 | 18 | 100 | 1800 | 0.45 | 810 |  |  | 4 | 10 | 15 | 13 | 0 |  |  | 0.4 | 0 | 2000 | 0 | 3 x 4.0 | SPARE
1A-P1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 30 | 14 |  | 225 |  | 0.45 | 500 | 250 | 2 | 3 x 2.5 | 1-AS2 - SOCKET POINTS
1-AL2 - LIGHTING POINTS | 2 x 1.5 | 18 | 100 | 1800 | 0.45 |  |  | 810 | 6 | 10 | 10 | 15 |  |  | 450 | 0.45 | 1000 | 1000 | 1 | 2 x 1.5 | 1-AL3 - LIGHTING POINTS
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.4 | 0 |  |  | 7 | 20 | 20 | 16 | 0 |  |  | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
1-AS1 - SOCKET POINTS | 3 x 2.5 | 5 | 250 | 1250 | 0.45 |  | 562.5 |  | 8 | 30 | 30 | 17 |  | 225 |  | 0.45 | 500 | 250 | 2 | 3 x 2.5 | 1-AS3 - SOCKET POINTS
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 15 | 18 |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.45 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 11400 |  | 2170 | 2042.5 | 1610 |  |  |  |  | 1200 | 1130 | 1650 |  | 7350
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3370 |  | 3172.5 | 3260 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 10302.5 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 12878.125 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 18 |  | A

## DB 2-A
FIRST FLOOR DISTRIBUTION BOARD (DB 2-A)
Location: | LOBBY | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB 2-A
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
2A-AC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 | 680 |  |  | 1 | 20 | 30 | 10 | 562.5 |  |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 2-AS1 - SOCKET POINTS
2A-AC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 2 | 20 | 20 | 11 |  | 1040 |  | 0.8 | 1300 | 1300 | 1 | 3 x 4.0 | 2A-AC2 - 20A SWITCH OUTLET
2-AS2 - SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 3 | 30 | 20 | 12 |  |  | 1200 | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 2A-WH1
2A-WH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 20 | 13 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | 2A-AC4 - 20A SWITCH OUTLET
2A-P1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 30 | 14 |  | 562.5 |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 2-AS3 - SOCKET POINTS
2-AL2 - LIGHTING POINTS | 2 x 1.5 | 10 | 100 | 1000 | 0.45 |  |  | 450 | 6 | 10 | 20 | 15 |  |  | 1200 | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 2A-WH3
2-AL3 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 | 450 |  |  | 7 | 10 | 10 | 16 | 315 |  |  | 0.45 | 700 | 100 | 7 | 2 x 1.5 | 2-AL5 - LIGHTING POINTS
2-AL1 - LIGHTING POINTS | 2 x 1.5 | 9 | 100 | 900 | 0.45 |  | 405 |  | 8 | 10 | 10 | 17 |  | 225 |  | 0.45 | 500 | 100 | 5 | 2 x 1.5 | 2-AL4 - LIGHTING POINTS
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 30 | 18 |  |  | 450 | 0.45 | 1000 | 250 | 4 | 3 x 2.5 | 2-AS4 - SOCKET POINTS
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 9100 |  | 2330 | 1885 | 900 |  |  |  |  | 1557.5 | 1827.5 | 2850 |  | 9850
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3887.5 |  | 3712.5 | 3750 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11850 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14812.5 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 20.7 |  | A

## DB 1-B
GROUND FLOOR DISTRIBUTION BOARD (DB 1-B)
Location: | PANTRY | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB 1-B
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
1B-AC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 1700 | 1700 | 0.8 | 1360 |  |  | 1 | 20 | 20 | 10 | 1200 |  |  | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 1B-WH1
1B-AC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 2 | 20 | 30 | 11 |  | 562.5 |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 1-BS1 - SOCKET POINTS
1B-P2 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  |  | 800 | 3 | 15 | 30 | 12 |  |  | 1200 | 0.4 | 3000 | 3000 | 1 | 3 x 6.0 | 1B-CCU1
SPARE | 3 x 4.0 | 0 | 850 | 0 | 0.8 | 0 |  |  | 4 | 15 | 15 | 13 | 0 |  |  | 0.4 | 0 | 2000 | 0 | 3 x 4.0 | SPARE
1B-P1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 30 | 14 |  | 225 |  | 0.45 | 500 | 250 | 2 | 3 x 2.5 | 1-BS2 - SOCKET POINTS
1-BL3 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 |  |  | 450 | 6 | 10 | 20 | 15 |  |  | 680 | 0.8 | 850 | 850 | 1 | 3 x 4.0 | 1B-AC2 - 20A SWITCH OUTLET
1-BL1 - LIGHTING POINTS | 2 x 1.5 | 13 | 100 | 1300 | 0.45 | 585 |  |  | 7 | 10 | 20 | 16 | 0 |  |  | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
1-BL2 - LIGHTING POINTS | 2 x 1.5 | 16 | 100 | 1600 | 0.45 |  | 720 |  | 8 | 10 | 30 | 17 |  | 225 |  | 0.45 | 500 | 250 | 2 | 3 x 2.5 | 1-BS3 - SOCKET POINTS
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 15 | 18 |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.45 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 10450 |  | 1945 | 2200 | 1250 |  |  |  |  | 1200 | 1012.5 | 1880 |  | 7600
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3145 |  | 3212.5 | 3130 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 9987.5 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 12484.375 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 17.4 |  | A

## DB 2-B
FIRST FLOOR DISTRIBUTION BOARD (DB 2-A)
Location: | LOBBY | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB 2-A
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
2B-AC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 | 680 |  |  | 1 | 20 | 30 | 10 | 562.5 |  |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 2-BS1 - SOCKET POINTS
2B-AC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 2 | 20 | 20 | 11 |  | 1040 |  | 0.8 | 1300 | 1300 | 1 | 3 x 4.0 | 2B-AC2 - 20A SWITCH OUTLET
2-BS2 - SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 3 | 30 | 20 | 12 |  |  | 1200 | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 2B-WH1
2B-WH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 20 | 13 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | 2B-AC4 - 20A SWITCH OUTLET
2B-P1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 30 | 14 |  | 562.5 |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 2-BS3 - SOCKET POINTS
2-BL2 - LIGHTING POINTS | 2 x 1.5 | 10 | 100 | 1000 | 0.45 |  |  | 450 | 6 | 10 | 20 | 15 |  |  | 1200 | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 2B-WH3
2-BL3 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 | 450 |  |  | 7 | 10 | 10 | 16 | 315 |  |  | 0.45 | 700 | 100 | 7 | 2 x 1.5 | 2-BL5 - LIGHTING POINTS
2-BL1 - LIGHTING POINTS | 2 x 1.5 | 9 | 100 | 900 | 0.45 |  | 405 |  | 8 | 10 | 10 | 17 |  | 225 |  | 0.45 | 500 | 100 | 5 | 2 x 1.5 | 2-BL4 - LIGHTING POINTS
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 30 | 18 |  |  | 450 | 0.45 | 1000 | 250 | 4 | 3 x 2.5 | 2-BS4 - SOCKET POINTS
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 9100 |  | 2330 | 1885 | 900 |  |  |  |  | 1557.5 | 1827.5 | 2850 |  | 9850
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3887.5 |  | 3712.5 | 3750 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11850 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14812.5 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 20.7 |  | A

## DB 1-C
GROUND FLOOR DISTRIBUTION BOARD (DB 1-C)
Location: | PANTRY | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB 1-C
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
1C-AC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 1700 | 1700 | 0.8 | 1360 |  |  | 1 | 20 | 20 | 10 | 1200 |  |  | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 1C-WH1
1C-AC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 2 | 20 | 20 | 11 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | 1C-AC2 - 20A SWITCH OUTLET
1C-P2 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  |  | 800 | 3 | 15 | 30 | 12 |  |  | 1200 | 0.4 | 3000 | 3000 | 1 | 3 x 6.0 | 1C-CCU1
SPARE | 3 x 4.0 | 0 | 850 | 0 | 0.8 | 0 |  |  | 4 | 15 | 15 | 13 | 0 |  |  | 0.4 | 0 | 2000 | 0 | 3 x 4.0 | SPARE
1C-P1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 30 | 14 |  | 225 |  | 0.45 | 500 | 250 | 2 | 3 x 2.5 | 1-BS2 - SOCKET POINTS
1-CL2 - LIGHTING POINTS | 2 x 1.5 | 14 | 100 | 1400 | 0.45 |  |  | 630 | 6 | 10 | 30 | 15 |  |  | 562.5 | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 1-BS1 - SOCKET POINTS
1-CL3 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 | 450 |  |  | 7 | 10 | 20 | 16 | 0 |  |  | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
1-CL1 - LIGHTING POINTS | 2 x 1.5 | 15 | 100 | 1500 | 0.45 |  | 675 |  | 8 | 10 | 30 | 17 |  | 225 |  | 0.45 | 500 | 250 | 2 | 3 x 2.5 | 1-BS3 - SOCKET POINTS
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 15 | 18 |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 10450 |  | 1810 | 2155 | 1430 |  |  |  |  | 1200 | 1130 | 1762.5 |  | 7600
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3010 |  | 3285 | 3192.5 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 9987.5 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 12484.375 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 17.4 |  | A

## DB 2-C
FIRST FLOOR DISTRIBUTION BOARD (DB 2-A)
Location: | LOBBY | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB 2-A
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
2C-AC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 | 680 |  |  | 1 | 20 | 30 | 10 | 562.5 |  |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 2-CS1 - SOCKET POINTS
2C-AC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 2 | 20 | 20 | 11 |  | 1040 |  | 0.8 | 1300 | 1300 | 1 | 3 x 4.0 | 2C-AC2 - 20A SWITCH OUTLET
2-CS2 - SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 3 | 30 | 20 | 12 |  |  | 1200 | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 2C-WH1
2C-WH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 20 | 13 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | 2C-AC4 - 20A SWITCH OUTLET
2C-P1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 30 | 14 |  | 562.5 |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 2-CS3 - SOCKET POINTS
2-CL2 - LIGHTING POINTS | 2 x 1.5 | 10 | 100 | 1000 | 0.45 |  |  | 450 | 6 | 10 | 20 | 15 |  |  | 1200 | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 2C-WH3
2-CL3 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 | 450 |  |  | 7 | 10 | 10 | 16 | 315 |  |  | 0.45 | 700 | 100 | 7 | 2 x 1.5 | 2-CL5 - LIGHTING POINTS
2-CL1 - LIGHTING POINTS | 2 x 1.5 | 9 | 100 | 900 | 0.45 |  | 405 |  | 8 | 10 | 10 | 17 |  | 225 |  | 0.45 | 500 | 100 | 5 | 2 x 1.5 | 2-CL4 - LIGHTING POINTS
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 30 | 18 |  |  | 450 | 0.45 | 1000 | 250 | 4 | 3 x 2.5 | 2-CS4 - SOCKET POINTS
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 9100 |  | 2330 | 1885 | 900 |  |  |  |  | 1557.5 | 1827.5 | 2850 |  | 9850
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3887.5 |  | 3712.5 | 3750 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11850 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14812.5 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 20.7 |  | A

## DB 1-D
GROUND FLOOR DISTRIBUTION BOARD (DB 1-D)
Location: | PANTRY | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB 1-D
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
1D-AC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 1700 | 1700 | 0.8 | 1360 |  |  | 1 | 20 | 20 | 10 | 1200 |  |  | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 1D-WH1
1D-AC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 2 | 20 | 20 | 11 |  | 680 |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | 1D-AC2 - 20A SWITCH OUTLET
1D-P2 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  |  | 800 | 3 | 15 | 30 | 12 |  |  | 1200 | 0.4 | 3000 | 3000 | 1 | 3 x 6.0 | 1D-CCU1
SPARE | 3 x 4.0 | 0 | 850 | 0 | 0.8 | 0 |  |  | 4 | 15 | 15 | 13 | 0 |  |  | 0.4 | 0 | 2000 | 0 | 3 x 4.0 | SPARE
1D-P1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 30 | 14 |  | 225 |  | 0.45 | 500 | 250 | 2 | 3 x 2.5 | 1-BS2 - SOCKET POINTS
1-DL2 - LIGHTING POINTS | 2 x 1.5 | 14 | 100 | 1400 | 0.45 |  |  | 630 | 6 | 10 | 30 | 15 |  |  | 562.5 | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 1-BS1 - SOCKET POINTS
1-DL3 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 | 450 |  |  | 7 | 10 | 20 | 16 | 0 |  |  | 0.8 | 0 | 1500 | 0 | 3 x 4.0 | SPARE
1-DL1 - LIGHTING POINTS | 2 x 1.5 | 15 | 100 | 1500 | 0.45 |  | 675 |  | 8 | 10 | 30 | 17 |  | 225 |  | 0.45 | 500 | 250 | 2 | 3 x 2.5 | 1-BS3 - SOCKET POINTS
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 15 | 18 |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.5 | 0 | 250 | 0 | 3 x 2.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 10450 |  | 1810 | 2155 | 1430 |  |  |  |  | 1200 | 1130 | 1762.5 |  | 7600
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3010 |  | 3285 | 3192.5 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 9987.5 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 12484.375 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 17.4 |  | A

## DB 2-D
FIRST FLOOR DISTRIBUTION BOARD (DB 2-A)
Location: | LOBBY | [12 empty] | Type: | 100A 6-WAYS TP&N MCB DISTRIBUTION BOARD (ABB) OR SCHNEIDER ELECTRIC
Voltage & Freq.: | 230/400V, 50Hz | [12 empty] | DB Ref.: | DB 2-A
Cable Length(m) to ControlPanel | [13 empty] | Fed from | CONTROL PANEL
DESIGNATION OF LOAD | CABLE SIZE (mm2) | No of points | Watts per point | Peak Load | Diversity Factor | PHASE LOAD IN WATTS |  |  | TRIP RATING |  |  |  | PHASE LOAD IN WATTS |  |  | Diversity Factor | Peak Load | Watts per point | No of points | CABLE SIZE (mm2) | DESIGNATION OF LOAD
[6 empty] | R | Y | B |  |  |  |  | R | Y | B
2D-AC1 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 | 680 |  |  | 1 | 20 | 30 | 10 | 562.5 |  |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 2-DS1 - SOCKET POINTS
2D-AC3 - 20A SWITCH OUTLET | 3 x 4.0 | 1 | 850 | 850 | 0.8 |  | 680 |  | 2 | 20 | 20 | 11 |  | 1040 |  | 0.8 | 1300 | 1300 | 1 | 3 x 4.0 | 2D-AC2 - 20A SWITCH OUTLET
2-DS2 - SOCKET POINTS | 3 x 2.5 | 4 | 250 | 1000 | 0.45 |  |  | 450 | 3 | 30 | 20 | 12 |  |  | 1200 | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 2D-WH1
2D-WH2 | 3 x 4.0 | 1 | 1500 | 1500 | 0.8 | 1200 |  |  | 4 | 20 | 20 | 13 | 680 |  |  | 0.8 | 850 | 850 | 1 | 3 x 4.0 | 2D-AC4 - 20A SWITCH OUTLET
2D-P1 - 15A POWER SOCKET | 3 x 4.0 | 1 | 2000 | 2000 | 0.4 |  | 800 |  | 5 | 15 | 30 | 14 |  | 562.5 |  | 0.45 | 1250 | 250 | 5 | 3 x 2.5 | 2-DS3 - SOCKET POINTS
2-DL2 - LIGHTING POINTS | 2 x 1.5 | 10 | 100 | 1000 | 0.45 |  |  | 450 | 6 | 10 | 20 | 15 |  |  | 1200 | 0.8 | 1500 | 1500 | 1 | 3 x 4.0 | 2D-WH3
2-DL3 - LIGHTING POINTS | 2 x 1.5 | 1 | 1000 | 1000 | 0.45 | 450 |  |  | 7 | 10 | 10 | 16 | 315 |  |  | 0.45 | 700 | 100 | 7 | 2 x 1.5 | 2-DL5 - LIGHTING POINTS
2-DL1 - LIGHTING POINTS | 2 x 1.5 | 9 | 100 | 900 | 0.45 |  | 405 |  | 8 | 10 | 10 | 17 |  | 225 |  | 0.45 | 500 | 100 | 5 | 2 x 1.5 | 2-DL4 - LIGHTING POINTS
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 | 9 | 30 | 30 | 18 |  |  | 450 | 0.45 | 1000 | 250 | 4 | 3 x 2.5 | 2-AS4 - SOCKET POINTS
SPARE | 3 x 2.5 | 0 | 250 | 0 | 0.5 | 0 |  |  |  | 30 | 30 |  | 0 |  |  | 0.45 | 0 | 1000 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 2.5 | 0 | 1500 | 0 | 0.8 |  | 0 |  |  | 20 | 30 |  |  | 0 |  | 0.4 | 0 | 6000 | 0 | 3 x 2.5 | SPARE
SPARE | 2 x 1.5 | 0 | 1000 | 0 | 0.45 |  |  | 0 |  | 10 | 10 |  |  |  | 0 | 0.7 | 0 | 60 | 0 | 2 x 1.5 | SPARE
SPARE | 3 x 4.0 | 0 | 1500 | 0 | 0.8 | 0 |  |  |  | 20 | 30 |  | 0 |  |  | 0.6 | 0 | 3000 | 0 | 3 x 6.0 | SPARE
SPARE | 3 x 4.0 | 0 | 2000 | 0 | 0.6 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1119 | 0 | 0.8 |  |  | 0 |  | 15 | 20 |  |  |  | 0 | 0.8 | 0 | 1492 | 0 | 3 x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 | 0 |  |  |  | 20 | 20 |  | 0 |  |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  | 0 |  |  | 20 | 20 |  |  | 0 |  | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SPARE | 3 x 4.0 | 0 | 1200 | 0 | 1 |  |  | 0 |  | 20 | 20 |  |  |  | 0 | 1 | 0 | 400 | 0 | 3x 4.0 | SPARE
SUB-TOTALS |  |  |  | 9100 |  | 2330 | 1885 | 900 |  |  |  |  | 1557.5 | 1827.5 | 2850 |  | 9850
* RING MAIN FINBL SUB-CIRCUITS | [10 empty] | 100A MCB; 300mA
DB LOAD CABLE SIZE: | [7 empty] | R |  | Y | B | [5 empty] | EARTH WIRE SIZE:
4C x 6mm² PVC/PVC COPPER CABLE | [5 empty] | CONNECTED (W) |  | 3887.5 |  | 3712.5 | 3750 | [5 empty] | 1 x 6mm² PVC SINGLE CORE COPPER CABLE
[6 empty] | SPARE(W) | [7 empty] | 500
DB ISOLATOR TYPE: | [5 empty] | TOTAL CONNECTED (W) | [7 empty] | 11850 |  | W
100A TP&N MCCB; 300mA | [5 empty] | POWER FACTOR | [7 empty] | 0.8 |  | Cos ф
[6 empty] | TOTAL CONNECTED (VA) | [7 empty] | 14812.5 |  | VA
[6 empty] | CURRENT (A) | [7 empty] | 20.7 |  | A